## Template
| NOTE: | Data in red are | Data in green are
|  | required | optional
Heat/Cooling Equipment Request for Information - Specification
Manufacturer
Heat Pump series
Model No.
SECTION A - SOURCE SIDE CAPACITY/POWER FACTORS
| Heat Pump Specifications for Cooling |  |  | Heat Pump Specifications for Heating
| Load Side EWT | 16 | ˚C | Load Side EWT | 35 | ˚C
| Flow Rate 1 | 180 | l/min | Flow Rate 1 | 180 | l/min
| Source EWT (Deg C) | Capacity (kW) | Power (kW) | Source EWT (Deg C) | Capacity (kW) | Power (kW)
| 25 | 115.5 | 12.8 | 0 | 66.1 | 15.3
| 30 | 98 | 13.8 | 10 | 94 | 14.8
| 35 | 107 | 15.1 | 20 | 130 | 15.5
| Load Side EWT | 16 | ˚C | Load Side EWT | 35 | ˚C
| Flow Rate 2 | 0 | l/min | Flow Rate 2 | 0 | l/min
| Source EWT (Deg C) | Capacity (kW) | Power (kW) | Source EWT (Deg C) | Capacity (kW) | Power (kW)
| 25 | 0 | 0 | 0 | 0 | 0
| 30 | 0 | 0 | 10 | 0 | 0
| 35 | 0 | 0 | 20 | 0 | 0
SECTION B - LOAD SIDE TEMP CORRECTION FACTORS
| Cooling Load Temperature Corrections |  |  | Heating Load Temperature Corrections
| Source EWT |  | ˚C | Source EWT | 0 | ˚C
| Load EWT (Deg C) | Capacity (kW) | Power (kW) | Load EWT (Deg C) | Capacity (kW) | Power (kW)
| 16 | 0 | 0 | 25 | 0 | 0
| 17 | 0 | 0 | 29 | 0 | 0
| 18 | 0 | 0 | 33 | 0 | 0
| 19 | 0 | 0 | 37 | 0 | 0
| 20 | 0 | 0 | 41 | 0 | 0
SECTION C - LOAD SIDE FLOW CORRECTION FACTORS
|  | Cooling |  |  | Heating
| Source EWT | 30 | ˚C | Source EWT | 0 | ˚C
| 100% Flow | 120 | l/min | 100% Flow | 120 | l/min
| % of Nominal | Capacity (kW) | Power (kW) | % of Nominal | Capacity (kW) | Power (kW)
| 80 | 0 | 0 | 80 | 0 | 0
| 90 | 0 | 0 | 90 | 0 | 0
| 100 | 0 | 0 | 100 | 0 | 0
| 110 | 0 | 0 | 110 | 0 | 0
| 120 | 0 | 0 | 120 | 0 | 0
| Notes | Section A: Keep Load Side temps the same throughout and arrive at the capacities from alteration of the Source Temps.
Section A: Carry out the same exercise however with a different flow rate to obtain source flow rate correction factors.
Section B: Keep the source EWT constant as indicated and arrive at the capacity and power by altering the load side EWT.
Section C: Keep the source temperatures constant and Vary the load flow to arrive at capacity figures.

## Sample Data from WFI pump
| NOTE: | Data in red are | Data in green are
|  | required | optional
Heat/Cooling Equipment Request for Information - Specification
| Manufacturer |  | WaterFurnace
| Heat Pump series |  | Premier Int'l 50 Hz
| Model No. |  | PK07
SECTION A - SOURCE SIDE CAPACITY/POWER FACTORS
| Heat Pump Specifications for Cooling |  |  | Heat Pump Specifications for Heating
| Load Side EWT | 19.4 | ˚C | Load Side EWT | 21.1 | ˚C
| Flow Rate 1 | 11.4 | l/min | Flow Rate 1 | 11.4 | l/min
| Source EWT (Deg C) | Capacity (kW) | Power (kW) | Source EWT (Deg C) | Capacity (kW) | Power (kW)
| 21.1 | 6.9 | 1.19 | -1.1 | 4.3 | 1.25
| 32.2 | 6.5 | 1.54 | 10 | 5.7 | 1.34
| 43.3 | 5.9 | 1.91 | 21.1 | 7 | 1.48
| Load Side EWT | 19.4 | ˚C | Load Side EWT | 21.1 | ˚C
| Flow Rate 2 | 22.8 | l/min | Flow Rate 2 | 22.8 | l/min
| Source EWT (Deg C) | Capacity (kW) | Power (kW) | Source EWT (Deg C) | Capacity (kW) | Power (kW)
| 21.1 | 7 | 1.1 | -1.1 | 4.7 | 1.31
| 32.2 | 6.6 | 1.42 | 10 | 6.1 | 1.39
| 43.3 | 6 | 1.75 | 21.1 | 7.4 | 1.54
SECTION B - LOAD SIDE TEMP CORRECTION FACTORS
| Cooling Load Temperature Corrections |  |  | Heating Load Temperature Corrections
NOTE: TO calculate all LOAD SIDE correction factors, what you need to calculate is the impact on pump capacity and power when you change 1 load side variable (temp or flow) while holding all other variables constant.
| Source EWT | 32.2 | ˚C | Source EWT | 10 | ˚C
EXAMPLE: LOAD SIDE TEMP CORRECTIONS, COOLING
| Load EWT (Deg C) | Capacity (kW) | Power (kW) | Load EWT (Deg C) | Capacity (kW) | Power (kW)
| 17.2 | 0.92 | 0.98 | 15.6 | 1.03 | 0.95 | We select a minimum of three Load EWTs (and max of 5) . The middle one should be the same load EWT used (19.4 in this case) when you determined the source side cooling factors. You will note that the source side cooling data lists 19.4 as the load side temp (meaning that temp is the normal/baseline value).
| 19.4 | 1 | 1 | 21.1 | 1 | 1 | The middle value (normal/baseline) has capacity and power factors of "1.000" by default
| 21.7 | 1.08 | 1.02 | 26.7 | 0.97 | 1.05 | Next, you look at the capacity and power of the pump when you have an EWT of 17.2 and you divide those capacity and power values by the capacity and power values of the pump whe the load EWT is at 19.4. Doing this division step creates the correction factor. Repeat for the 21.7 temperature.
|  |  |  | 37 | 61.5 | 14.8
|  |  |  | 41 | 60 | 16.1
|  | SECTION C - LOAD SIDE FLOW CORRECTION FACTORS |  |  |  |  | EXAMPLE:LOAD FLOW CORRECTION FACTORS, COOLING
We again need a minimum of 3 flow rates (and a max of 5). Note that the flow rates are expressed in terms of "% of nominal flow".
|  | Cooling |  |  | Heating |  | Choose one flow rate as your standard (in this case it is 283 l/second), select the middle source side EWT (same as before), and then determine the pump capacity and power.
Choose a flow rate that is below the standard and divide it by the standard to come up with a %. Then, divide the capacity and power at the lower flow right by the capacity and power at the standard flow rate to come up with the ratio correction factors. Repeat.
| Source EWT | 32.2 | ˚C | Source EWT | 10 | ˚C
| 100% Flow | 283 | l/second | 100% Flow | 283 | l/second | For Water to Air pumps, load side correction factors (temp and flow) aren't critical. For water to water pumps, they can be quite important.
| % of Nominal | Capacity (kW) | Power (kW) | % of Nominal | Capacity (kW) | Power (kW)
| 83.3 | 0.977 | 0.98 | 83.3 | 0.98 | 1.03
| 100 | 1 | 1 | 100 | 1 | 1
| 117 | 1.023 | 1.03 | 117 | 1.024 | 0.978
| 110 | 0 | 0 | 110 | 0 | 0
| 120 | 0 | 0 | 120 | 0 | 0
| Notes | Section A: Keep Load Side temps the same throughout and arrive at the capacities from alteration of the Source Temps.
Section A: Carry out the same exercise however with a different flow rate to obtain source flow rate correction factors.
Section B: Keep the source EWT constant as indicated and arrive at the capacity and power by altering the load side EWT.
Section C: Keep the source temperatures constant and Vary the load flow to arrive at capacity figures.